## Start Here
Welcome to the Heat Calculation Program!
This program is intended to assist you in determining the Btu requirements (and thus number of our heaters) needed for a specific greenhouse operation. To begin…
1. Determine style of house (Quonset, Gable, or Arch), and click on appropriate tab based on type of house.
Within the selected tab…
2. Fill in specific dimensions under 'House Data' (width, height, etc.).
3. Under 'Design Data', determine and select from the drop down list the average Wind Velocity (based on specific area of country).
4. Determine and select from the drop down the Temperature Differential, based on average outside low temperatures and desired interior greenhouse temperature. For example, if the average outside temperature is 15oF and the interior greenhouse temperature is set at 65oF, the temperature differential will be 50. The Temp Map and Heat Zone Map tabs show average temps for a normal winter
5. Select from the drop down either new or old construction for the Combustion/Infiltration field.
6. Choose appropriate building materials from the drop downs for each section of greenhouse under House Materials based on materials used in roof and walls of structure.
7. Choose appropriate construction type from the drop downs for each section of greenhouse under Basic Construction Style, based on materials used.
8. The spreadsheet will automatically calculate area, heat loss and the recommended quantity of Therma Grow® 120 or 220 or Bloom® 400 unit heaters required.
The Form Data tab has all the raw data used within the sheets. Refer to this tab to review if needed.
If you need help, have questions, or find data is missing from this program, please contact our Technical Support Department at 608-779-6101.

## Temp Map
Temperature Map for United States

## Heat Zone Map
Heat Zone Map for United States

## Quonset House
Quonset Type House - Heating Needs
House Data:
Width, W | 0
Length, L | 0
Sidewall Height, H | 0
Center Height, G | 0
Number of Bays | 0
Design Data:
Wind Factor (MPH) | 15 | 1
Temperature Differential (Deg.) | 5 | 5
Combustion / Infiltration Factor | New Construction | 1.25
House Materials |  |  | AREA CALCULATIONS
Area AB | Corrugated FRP Panels | 1.2 | Area AB | 0
Area C | Concrete, poured 8 in. | 0.58 | Area C | 0
Area D | Concrete block, 8 in. | 0.51 | Area D | 0
Area E | Single film plastic | 1.2 | Area E | 0
|  |  | Volume | 0
Basic Construction Style
Area AB | Fiberglass on metal frame | 1.03 | HEAT LOSS CALCULATIONS
Area C | Fiberglass on metal frame | 1.03 | Area AB | 0
Area D | Fiberglass on metal frame | 1.03 | Area C | 0 | Qty. Therma Grow 220 req. | 0
Area E | Fiberglass on metal frame | 1.03 | Area D | 0 | Qty. Therma Grow 120 req. | 0
|  |  | Area E | 0
|  |  | Total Air | 0 | Qty.Bloom 400 req. | 0
|  |  | Total | 0
Your Data
B
A
C
E
D
H
G
W
L

## Gable House
Gable Type Houses - Heating Needs
House Data:
Width, W | 0
Length, L | 0
Sidewall Height, H | 0
Gable Height, G | 0
Number of Bays | 0
Design Data:
Wind Factor (MPH) | 15 | 1
Temperature Differential (Deg.) | 5 | 5
Combustion / Infiltration Factor | New Construction | 1.25
House Materials |  |  | AREA CALCULATIONS
Area A | Cement asbestos board | 1.15 | Area A | 0
Area B | Cement asbestos board | 1.15 | Area B | 0
Area C | Glass, double layer, 1/4 in. space | 0.65 | Area C | 0
Area D | Glass, single layer | 1.13 | Area D | 0
|  |  | Volume | 0
Basic Construction Style
Area A | Fiberglass on metal frame | 1.03 | HEAT LOSS CALCULATIONS
Area B | Fiberglass on metal frame | 1.03 | Area A | 0
Area C | Fiberglass on metal frame | 1.03 | Area B | 0 | Qty. Therma Grow 220 req. | 0
Area D | Fiberglass on metal frame | 1.03 | Area C | 0 | Qty. Therma Grow 120 req. | 0
|  |  | Area D | 0
|  |  | Total Air | 0 | Qty. Bloom 400 req. | 0
|  |  | Total | 0
A
B
C
D
H
G
W
L
Your Data

## Arch house
Arch Type Houses - Heating Needs
House Data:
Width, W | 0
Length, L | 0
Sidewall Height, H | 0
Arch Height, G | 0
Number of Bays | 0
Design Data:
Wind Factor (MPH) | 15 | 1
Temperature Differential (Deg.) | 5 | 5
Combustion / Infiltration Factor | New Construction | 1.25
House Materials |  |  | AREA CALCULATIONS
Area A | Concrete block, 4 in. | 0.64 | Area A | 0
Area B | Concrete, poured, 4 in. | 1.15 | Area B | 0
Area C | Double film plastic, inflated | 0.7 | Area C | 0
Area D | Corrugated FRP Panels | 1.2 | Area D | 0
|  |  | Volume | 0
Basic Construction Style
Area A | Fiberglass on metal frame | 1.03 | HEAT LOSS CALCULATIONS
Area B | Fiberglass on metal frame | 1.03 | Area A | 0
Area C | Fiberglass on metal frame | 1.03 | Area B | 0 | Qty. Therma Grow 220 req. | 0
Area D | Fiberglass on metal frame | 1.03 | Area C | 0 | Qty. Therma Grow 120 req. | 0
|  |  | Area D | 0
|  |  | Total Air | 0 | Qty. Bloom 400 req. | 0
|  |  | Total | 0
Your Data
D
A
C
B
L
W
H
G

## Form Data
Heat Transfer Coefficients (1,2)
| Material |  | Wind Velocity Factor (2)
| Coverings | Btu/sq ft - Deg F- hr | MPH | W
| Corrugated FRP Panels | 1.2 | 15 | 1 | gg
| Double film plastic, inflated | 0.7 | 20 | 1.04
| Double plastic over glass | 0.6 | 25 | 1.08
| Fiberglass | 1 | 30 | 1.12
| Glass, double layer, 1/4 in. space | 0.65 | 35 | 1.16
| Glass, single layer | 1.13
| Single film plastic | 1.2
| Single film plastic over glass | 0.85
| Walls |  | Air Exchange:
| Cement asbestos board | 1.15
| Cement asbestos board, plus 1 in. polystyrene | 0.21 | New Construction:
| Cement asbestos board, plus 1 in. urethane | 0.14 | LBW targets a total air exchange of 1.25, infiltration plus
| Concrete block, 4 in. | 0.64 | combustion for new construction.
| Concrete block, 8 in. | 0.51
| Concrete block, 8 in. + 1 in. polystyrene | 0.18 | Old Construction:
| Concrete block, 8 in. + 1 in. urethane foam | 0.13 | LBW targets for a total air exchange of 2.0, infiltration plus
| Concrete, poured 8 in. | 0.58 | combustion for old construction
| Concrete, poured, 4 in. | 1.15
| Concrete, poured, 6 in. | 0.75 | In cases of extremely high wind multiply air exchange factor by
wind velocity factor W.
Construction Style, Coverings (2)
| Fiberglass on metal frame | 1.03
| Film plastic on metal frame | 1.02
| Film plastic or fiberglass on wood | 1
| Metal Frame and glazing system, 16-24 in. spacing | 1.08
| Metal Frame and glazing system, 48 in. spacing | 1.05
(1) Texas Greenhouse Management Handbook
(2) NGMA Standards for Heat Loss In Greenhouse Structures
Temp | New Construction | 1.25
5 | Old Construction | 2
10
15 |  |  |  |  | Cement asbestos board | 1.15
20 |  |  |  |  | Cement asbestos board, plus 1 in. polystyrene | 0.21
25 |  |  |  |  | Cement asbestos board, plus 1 in. urethane | 0.14
30 |  |  |  |  | Concrete block, 4 in. | 0.64
35 |  |  |  |  | Concrete block, 8 in. | 0.51
40 |  |  |  |  | Concrete block, 8 in. + 1 in. polystyrene | 0.18
45 |  |  |  |  | Concrete block, 8 in. + 1 in. urethane foam | 0.13
50 |  |  |  |  | Concrete, poured 8 in. | 0.58
55 |  |  |  |  | Concrete, poured, 4 in. | 1.15
60 |  |  |  |  | Concrete, poured, 6 in. | 0.75
65 |  |  |  |  | Corrugated FRP Panels | 1.2
70 |  |  |  |  | Double film plastic, inflated | 0.7
75 |  |  |  |  | Double plastic over glass | 0.6
80 |  |  |  |  | Fiberglass | 1
85 |  |  |  |  | Glass, double layer, 1/4 in. space | 0.65
90 |  |  |  |  | Glass, single layer | 1.13
95 |  |  |  |  | Single film plastic | 1.2
100 |  |  |  |  | Single film plastic over glass | 0.85